## BOQ
BILL OF QUANTITIES — FIRE ALARM & VOICE EVACUATION SYSTEM
Drawing ICC-DLRC-SIG2-SD-MEP/FA-109 Rev 01 (15.09.2026) — Level 02 to 10 & 12 to 16 (typical floor × 14)
Quantities counted from the DXF. Rate and Amount columns are blank for the estimator. See 'Assumptions & Notes' for basis and open items.
Item | Description | Model / Type | Mounting height | Unit | Qty per typical floor | No. of floors | Total qty | Rate (AED) | Amount (AED) | Remarks
A. AUTOMATIC DETECTION DEVICES
A.1 | Intelligent photoelectric smoke detector complete with standard mounting base | SIGA-OSD-FCN + SIGA-SB | Ceiling mounted | Nos | 32 | 14 | 448 |  |  | Typical floor coverage. 36 symbols on plan less the 4 noted 'L6 & L12 only' below.
A.2 | Intelligent photoelectric smoke detector with standard base — additional units at Level 06 & 12 only | SIGA-OSD-FCN + SIGA-SB | Ceiling mounted | Nos | 4 | 2 | 8 |  |  | Drawing note: 'SD LOCATED ONLY IN LEVEL-6 & 12'.
A.3 | Intelligent photoelectric smoke detector complete with isolator base | SIGA-OSD-FCN + SIGA-IB | Ceiling mounted | Nos | 5 | 14 | 70 |  |  | Loop isolation per general note 4.
A.4 | Intelligent photoelectric smoke detector complete with sounder base | SIGA-OSD-FCN + SIGA-LPS | Ceiling mounted | Nos | 31 | 14 | 434 |  |  | Apartment sounder coverage; fed by the 24 V DC circuit.
A.5 | Intelligent multi-sensor detector (optical + heat) with standard base | SIGA-OSHD-FCN + SIGA-SB | Ceiling mounted | Nos | 26 | 14 | 364 |  |  | Kitchens / high-nuisance areas.
A.6 | Intelligent rate-of-rise heat detector complete with isolator base | SIGA-HRD-FCN + SIGA-IB | Ceiling mounted | Nos | 1 | 14 | 14
B. MANUAL CALL POINTS, MODULES & INTERFACE DEVICES
B.1 | Addressable manual call point (break glass), surface type | SIGA-278 | 1200 mm from FFL | Nos | 3 | 14 | 42 |  |  | Mounts on 3"×3" G.I. back box — see item D.3.
B.2 | Addressable control relay module | SIGA-CR | As per site condition | Nos | 4 | 14 | 56 |  |  | Interface to MSFD / smoke control / sliding doors / ZCV.
B.3 | Addressable control relay module — even levels only | SIGA-CR | As per site condition | Nos | 2 | 8 | 16 |  |  | Drawing note: 'CR LOCATED ONLY IN LEVEL-02,04,06,08,10,12,14,16 ONLY'.
B.4 | Addressable dual input monitor module | SIGA-CT2 | As per site condition | Nos | 1 | 14 | 14 |  |  | 2 loop addresses.
B.5 | Addressable dual input riser module | SIGA-CC2A | As per site condition | Nos | 1 | 14 | 14 |  |  | Speaker circuit riser — returns to CC2A at telecom room.
B.6 | End-of-line resistor | As per manufacturer | — | Nos | 1 | 14 | 14
B.7 | Fire telephone jack, flush type | 6830-3 | 1200 mm from FFL | Nos | 3 | 14 | 42 |  |  | Mounts on 2"×4" G.I. concealed back box — see item D.4.
C. VOICE EVACUATION & AUDIBLE DEVICES
C.1 | Ceiling mounted fire alarm speaker complete with fire dome | EST-S186C | Ceiling mounted | Nos | 13 | 14 | 182 |  |  | Speaker circuit CK4, addresses SP1–SP13.
C.2 | Voice evacuation amplifier | APS6A/230 | 1800 mm from FFL (top of panel) | Nos | 1 | 3 | 3 |  |  | Drawing note: 'AMPLIFIERS LOCATED ONLY IN LEVEL-03/09/15'.
D. PANELS, POWER SUPPLY, CABLES & ACCESSORIES
D.1 | Sub fire alarm control panel | EST4 | 1800 mm from FFL (top of panel) | Nos | 1 | 1 | 1 |  |  | Drawing note: 'SUB FIRE ALARM CONTROL PANEL LOCATED AT L10 ONLY'.
D.2 | Booster power supply | BPS10A/230 | 1800 mm from FFL (top of panel) | Nos | 1 | 1 | 1 |  |  | Drawing note: 'BOOSTER POWER SUPPLY LOCATED ONLY IN LEVEL-09'.
D.3 | Detection loop cable, 2C × 1.5 mm² fire rated | 2C×1.5 mm² FR | In 25 mm Ø PVC conduit | Mtr | 654 | 14 | 10072 |  |  | Measured route length on layer FA-LOOP CABLE. Loop 3 and Loop 4 pass this floor.
D.4 | 24 V DC power cable to sounder bases, 2C × 2.5 mm² fire rated | 2C×2.5 mm² FR | In 25 mm Ø PVC conduit | Mtr | 358 | 14 | 5513 |  |  | Measured route length on layer FA-24V DC CIRCUIT.
D.5 | Voice evacuation speaker circuit cable, 2C × 2.5 mm² fire rated | 2C×2.5 mm² FR | In 25 mm Ø PVC conduit | Mtr | 157 | 14 | 2418 |  |  | Measured route length on layer VE-SPEAKER CIRCUIT.
D.6 | Fire telephone cable, 2C × 1.5 mm² fire rated | 2C×1.5 mm² FR | In 25 mm Ø PVC conduit | Mtr | TBA | — | TBA |  |  | NOT ROUTED ON THIS DRAWING — quantity to be taken from the riser / schematic.
D.7 | Data / network cable between panels, 2C × 1.5 mm² fire rated | 2C×1.5 mm² FR | In 25 mm Ø PVC conduit | Mtr | TBA | — | TBA |  |  | Only a riser stub shown — quantity to be taken from the riser / schematic.
D.8 | PVC conduit 25 mm Ø, embedded in slab / wall, with all fittings | 25 mm Ø PVC | Concealed | Mtr | 1169 | 14 | 18003 |  |  | Sum of the three routed circuits; assumes one conduit per circuit route.
D.9 | G.I. back box 3"×3" for manual call point | 3"×3" G.I. | 1200 mm from FFL | Nos | 3 | 14 | 42 |  |  | Per legend mounting note.
D.10 | G.I. back box 2"×4" concealed, for fire telephone jack | 2"×4" G.I. | 1200 mm from FFL | Nos | 3 | 14 | 42 |  |  | Per legend mounting note.
D.11 | Conduit sleeve / slab opening for vertical riser penetration | — | — | Nos | 3 | 14 | 42 |  |  | Riser penetrations shown on the typical floor.
| TOTAL — FIRE ALARM & VOICE EVACUATION (Level 02–10 & 12–16) | [7 empty] | 0
Legend: blue = counted / input value • green = floor multiplier from 'Assumptions & Notes' • black bold = calculated total • yellow = enter your rate
Cable and conduit totals include the wastage allowance set on the 'Assumptions & Notes' sheet.

## Assumptions & Notes
FIRE ALARM BOQ — BASIS OF QUANTITIES
Drawing | ICC-DLRC-SIG2-SD-MEP/FA-109 | Title block, layout 'OVERALL'
Title | LEVEL-02 TO 10 & 12 TO 16 FLOOR FIRE ALARM & VOICE EVACUATION SYSTEM LAYOUT
Revision / Date | 01 — 15.09.2026 — REVISED AS PER COMMENTS | Rev 00 issued for approval 31-07-2026
Scale | 1:200 | Model space units = millimetres
Drawn / Checked | RAMADAN / ASIF
System | EST4 addressable, Edwards/EST SIGA-series devices + voice evacuation | From drawing legend
INPUT CELLS (blue = edit these; all BOQ totals recalculate)
Typical floors covered by this drawing | 14 | L2–L10 (9 floors) + L12–L16 (5 floors). Excludes L11.
Floors with 'CR ONLY IN LEVEL 02,04,06,08,10,12,14,16' | 8 | Drawing note beside 2 nos control relay modules.
Floors with 'SD LOCATED ONLY IN LEVEL-6 & 12' | 2 | Drawing note beside 4 nos smoke detectors.
Floors with 'AMPLIFIERS LOCATED ONLY IN LEVEL-03/09/15' | 3 | Drawing note beside amplifier symbol.
Floors with 'SUB FACP LOCATED AT L10 ONLY' | 1 | Drawing note beside SFACP symbol.
Floors with 'BOOSTER POWER SUPPLY ONLY IN LEVEL-09' | 1 | Drawing note beside BPS symbol.
Wastage / site-routing allowance on cable & conduit | 10% | Applied to cable and conduit totals only.
HOW THE QUANTITIES WERE DERIVED
Device quantities are a machine count of the symbol blocks placed on the typical-floor plan in the DXF model space (plan area X 1,182,957 to 1,248,207 / Y -103,142 to -66,592 in model space).
Legend symbols and the installation-detail sketches on the same sheet were excluded from the count by coordinate zone, so nothing is double counted.
Two independent cross-checks agree with the block count:
• Detectors: 36 OS + 5 OSI + 31 LPS + 26 MS + 1 HI = 99. Device tags on the sheet read D16–D100 (85 on Loop 3) + D251–D260 (10 on Loop 4) = 95, plus the 4 detectors noted 'L6 & L12 only' which sit outside the tag sequence. 95 + 4 = 99. ✓
• Modules: 6 CR + 3 break glass + 1 CT2 + 1 CC2 = 11 devices = 13 loop addresses (CT2 and CC2 are dual-input). Module tags read M132–M138 and M140–M145 = 13 addresses. ✓
• Speakers: 13 ceiling speaker symbols vs speaker tags SP1–SP13 = 13. ✓
Cable lengths are the true polyline length of each routing layer inside the plan area (FA-LOOP CABLE, FA-24V DC CIRCUIT, VE-SPEAKER CIRCUIT), converted mm → m. They are horizontal run only.
Conduit is taken as the sum of the three circuit routes, per the legend note that every circuit runs inside 25mm Ø PVC conduit embedded in slab/wall.
ITEMS TO VERIFY BEFORE PRICING — the drawing does not settle these
Vertical drops not included | Cable lengths are the plan (horizontal) run only. Add drops to device height, riser rises between floors, and panel terminations. Typical addition 15–25%.
Fire telephone cable not routed | The legend lists a fire telephone cable (2C×1.5mm² FR) and 3 telephone jacks are placed, but no routing polyline exists on the sheet. Quantity carried as 'to be advised'.
Data / network cable not routed | Only a 1 m riser stub is drawn on layer FA-DATA NETWORK CABLE. Inter-panel network cable must come from the riser diagram.
No wall speakers, sounder-flashers or staircase speakers on this floor | Blocks WS, SF, SF-WP, CF and WSF-WP exist in the legend but are placed zero times on the plan. Confirm staircase / lobby audibility is covered by another drawing, or the floor is short of coverage.
Isolator count vs general note 4 | Note 4 requires an isolator base every 15 detectors. This floor has 99 detectors and 6 isolator bases (5 OSI + 1 HI) = 1 per 16.5. Isolators are counted per loop across floors, so confirm against the loop schematic.
Speaker circuit returns off-sheet | Note reads 'SPEAKER CIRCUIT RETURN TO CC2A @ TEL RM'. Riser lengths are outside this drawing.
2 nos heat detector symbols outside the plan | Two HD blocks sit at X ≈ -1,200,000 on layer E-670-M_FSP_FSA-1, far outside the floor plate — orphan content from another drawing. Excluded from the BOQ. Confirm they are not required.
Fire dome, back boxes and terminations | Carried per the legend's mounting notes. Confirm against the manufacturer's installation detail before ordering.

## Device Schedule
TYPICAL-FLOOR DEVICE SCHEDULE — as placed on drawing ICC-DLRC-SIG2-SD-MEP/FA-109 Rev 01
One row per symbol on the typical floor plan. The tag column is the nearest device label found in the drawing; blank where no label sits within 2.5 m.
# | Symbol | Device / model | Device tag on drawing | X (mm) | Y (mm) | Tag distance (mm)
1 | BPS | Booster power supply (BPS10A/230) | FACP01-GF/LP3/D17 | 1192414 | -98801 | 714
2 | CC2 | Dual input riser module (SIGA-CC2A) | FACP01-GF/LP3/D16 | 1192469 | -99713 | 1280
3 | CR | Control relay module (SIGA-CR) | AMP03-P3/CK4/SP8 | 1200217 | -88402 | 1927
4 | CR | Control relay module (SIGA-CR) |  | 1189517 | -90227
5 | CR | Control relay module (SIGA-CR) | AMP03-P3/CK4/SP5 | 1227250 | -94870 | 1233
6 | CR | Control relay module (SIGA-CR) | FACP01-GF/LP3/D32 | 1218098 | -96370 | 976
7 | CR | Control relay module (SIGA-CR) | FACP01-GF/LP3/D23 | 1203394 | -96370 | 1568
8 | CR | Control relay module (SIGA-CR) | FACP01-GF/LP3/D37 | 1225015 | -96370 | 1404
9 | CS | Ceiling speaker (EST-S186C) | FACP01-GF/LP3/D99 | 1190157 | -70794 | 1510
10 | CS | Ceiling speaker (EST-S186C) | AMP03-P3/CK4/SP12 | 1190157 | -78771 | 1516
11 | CS | Ceiling speaker (EST-S186C) | FACP01-GF/LP3/D73 | 1201396 | -85986 | 888
12 | CS | Ceiling speaker (EST-S186C) | FACP01-GF/LP3/D87 | 1190157 | -86768 | 774
13 | CS | Ceiling speaker (EST-S186C) | AMP03-P3/CK4/SP7 | 1201352 | -91601 | 478
14 | CS | Ceiling speaker (EST-S186C) | AMP03-P3/CK4/SP9 | 1192744 | -92279 | 787
15 | CS | Ceiling speaker (EST-S186C) | FACP01-GF/LP3/D82 | 1190157 | -94749 | 793
16 | CS | Ceiling speaker (EST-S186C) | AMP03-P3/CK4/SP6 | 1236637 | -95542 | 419
17 | CS | Ceiling speaker (EST-S186C) | AMP03-P3/CK4/SP5 | 1228626 | -95542 | 358
18 | CS | Ceiling speaker (EST-S186C) | AMP03-P3/CK4/SP4 | 1220640 | -95542 | 675
19 | CS | Ceiling speaker (EST-S186C) | AMP03-P3/CK4/SP3 | 1212627 | -95542 | 469
20 | CS | Ceiling speaker (EST-S186C) | AMP03-P3/CK4/SP2 | 1204638 | -95542 | 274
21 | CS | Ceiling speaker (EST-S186C) | AMP03-P3/CK4/SP1 | 1196639 | -95542 | 274
22 | CT2 | Dual input monitor module (SIGA-CT2) | AMP03-P3/CK4/SP11 | 1189737 | -87919 | 1953
23 | EOL | End-of-line resistor | FACP01-GF/LP3/D92 | 1196650 | -82391 | 2098
24 | FIRE PHONE JACK | Fire telephone jack (6830-3) | FACP01-GF/LP3/D75 | 1192833 | -89442 | 2269
25 | FIRE PHONE JACK | Fire telephone jack (6830-3) | AMP03-P3/CK4/SP9 | 1193515 | -93942 | 1417
26 | FIRE PHONE JACK | Fire telephone jack (6830-3) | FACP01-GF/LP3/M136 | 1223531 | -94042 | 1761
27 | HI | Heat detector, isolator base (SIGA-HRD-FCN + SIGA-IB) | FACP01-GF/LP3/D40 | 1231955 | -97542 | 273
28 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP4/D258 | 1183507 | -66592 | 274
29 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP4/D260 | 1196807 | -66592 | 2157
30 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP4/D256 | 1183257 | -73792 | 292
31 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D97 | 1197057 | -73792 | 451
32 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP4/D253 | 1183257 | -77367 | 440
33 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D93 | 1197057 | -77367 | 424
34 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP4/D252 | 1183257 | -81317 | 309
35 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D92 | 1197057 | -81317 | 1994
36 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D63 | 1225607 | -88092 | 1005
37 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D52 | 1244407 | -88142 | 654
38 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D51 | 1247557 | -88217 | 813
39 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D71 | 1207607 | -88242 | 630
40 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D66 | 1218558 | -88285 | 1886
41 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D84 | 1183182 | -88317 | 413
42 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D58 | 1237007 | -88642 | 1208
43 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D62 | 1229145 | -88642 | 1489
44 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D60 | 1233020 | -88692 | 1037
45 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D83 | 1183182 | -92167 | 570
46 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D50 | 1248207 | -94242 | 1535
47 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D49 | 1248044 | -96842 | 1740
48 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D34 | 1221657 | -102442 | 1858
49 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D26 | 1210707 | -102442 | 1093
50 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D48 | 1247907 | -102842 | 698
51 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D77 | 1192157 | -102892 | 2069
52 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D78 | 1182957 | -102892 | 1401
53 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D47 | 1244407 | -102942 | 276
54 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D31 | 1218007 | -103042 | 387
55 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D22 | 1203382 | -103042 | 914
56 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D21 | 1199632 | -103042 | 423
57 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D39 | 1233157 | -103142 | 965
58 | LPS | Smoke detector, sounder base (SIGA-OSD-FCN + SIGA-LPS) | FACP01-GF/LP3/D38 | 1229157 | -103142 | 745
59 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D100 | 1192560 | -69792 | 463
60 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D99 | 1187780 | -69792 | 1096
61 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP4/D255 | 1187505 | -74288 | 2000
62 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D96 | 1193057 | -74292 | 369
63 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D94 | 1193057 | -77013 | 241
64 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D95 | 1187505 | -77014 | 1283
65 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP4/D251 | 1187495 | -81658 | 568
66 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D91 | 1193007 | -81664 | 393
67 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D86 | 1187851 | -84536 | 711
68 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D64 | 1226007 | -92092 | 362
69 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D57 | 1236307 | -92642 | 912
70 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D59 | 1233507 | -92642 | 999
71 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D61 | 1228707 | -92642 | 1199
72 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D68 | 1214526 | -93071 | 430
73 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D69 | 1211212 | -93247 | 830
74 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D55 | 1240976 | -94242 | 944
75 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | AMP03-P3/CK4/SP10 | 1187874 | -96022 | 946
76 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D56 | 1240857 | -96842 | 1269
77 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D43 | 1237007 | -97842 | 668
78 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D29 | 1213938 | -97842 | 1145
79 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D27 | 1207601 | -97867 | 2031
80 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D36 | 1224720 | -97886 | 438
81 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D19 | 1195230 | -97914 | 400
82 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D33 | 1222207 | -98442 | 2031
83 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/D27 | 1210207 | -98442 | 675
84 | MS | Multi-sensor detector (SIGA-OSHD-FCN + SIGA-SB) | FACP01-GF/LP3/M132/133 | 1190349 | -99666 | 1149
85 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP4/D257 | 1183813 | -70229 | 583
86 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D98 | 1196507 | -70242 | 1976
87 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D99 | 1190157 | -70276 | 1330
88 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | AMP03-P3/CK4/SP12 | 1190157 | -78276 | 1757
89 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D89 | 1195732 | -84742 | 1934
90 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D85 | 1183807 | -84892 | 674
91 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D73 | 1201357 | -85512 | 493
92 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D87 | 1190157 | -86276 | 291
93 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) |  | 1205143 | -86636
94 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/M140 | 1197572 | -86636 | 1136
95 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/M140 | 1196156 | -88114 | 1995
96 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D70 | 1210857 | -89192 | 1732
97 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) |  | 1222057 | -89391
98 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D74 | 1201357 | -91112 | 240
99 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D75 | 1192735 | -91794 | 906
100 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) |  | 1197572 | -91960
101 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) |  | 1205143 | -91999
102 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D53 | 1244989 | -92353 | 2179
103 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D72 | 1206857 | -93692 | 250
104 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D82 | 1190157 | -94276 | 384
105 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | AMP03-P3/CK4/SP6 | 1236157 | -95542 | 798
106 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | AMP03-P3/CK4/SP5 | 1228157 | -95542 | 398
107 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | AMP03-P3/CK4/SP4 | 1220157 | -95542 | 873
108 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | AMP03-P3/CK4/SP2 | 1204157 | -95542 | 750
109 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | AMP03-P3/CK4/SP1 | 1196157 | -95542 | 746
110 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D17 | 1193457 | -97517 | 941
111 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D41 | 1230132 | -97542 | 1540
112 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D46 | 1243605 | -98695 | 933
113 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D79 | 1184007 | -99442 | 274
114 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D16 | 1193157 | -99803 | 593
115 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D45 | 1240507 | -101917 | 2009
116 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D35 | 1225439 | -102401 | 278
117 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D30 | 1214293 | -102451 | 300
118 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D44 | 1236979 | -102481 | 451
119 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D25 | 1207083 | -102487 | 456
120 | OS | Smoke detector, standard base (SIGA-OSD-FCN + SIGA-SB) | FACP01-GF/LP3/D20 | 1196047 | -102489 | 391
121 | OSI | Smoke detector, isolator base (SIGA-OSD-FCN + SIGA-IB) | FACP01-GF/LP3/D90 | 1192932 | -83792 | 235
122 | OSI | Smoke detector, isolator base (SIGA-OSD-FCN + SIGA-IB) | FACP01-GF/LP3/D67 | 1214907 | -88692 | 1647
123 | OSI | Smoke detector, isolator base (SIGA-OSD-FCN + SIGA-IB) | FACP01-GF/LP3/D54 | 1240507 | -89167 | 721
124 | OSI | Smoke detector, isolator base (SIGA-OSD-FCN + SIGA-IB) | AMP03-P3/CK4/SP3 | 1212157 | -95542 | 937
125 | OSI | Smoke detector, isolator base (SIGA-OSD-FCN + SIGA-IB) | FACP01-GF/LP3/D80 | 1183804 | -95588 | 1460
126 | PULL | Manual call point / break glass (SIGA-278) | FACP01-GF/LP3/M144 | 1191057 | -86454 | 684
127 | PULL | Manual call point / break glass (SIGA-278) | FACP01-GF/LP3/M137 | 1223685 | -94869 | 1574
128 | PULL | Manual call point / break glass (SIGA-278) | FACP01-GF/LP3/M141 | 1192968 | -94886 | 582
| Total symbols on typical floor | 128