## main
EDWARDS | PROJECT : Samana IVY Garden-2 (1B+G+4P+35+Roof) Residential Building @ PLOT NO: 648-8523, Wadi Al Safa 5, DLRC, Dubai, UAE |  |  |  |  | EST4
CLIENT | M/s. Samana IFM Holding Ltd
CONSULTANT | M/s. Al Hilal Engineering Consultant
CONTRACTOR | M/s. ITALTECH CONTRACTING L.L.C
FIRE ALARM SYSTEM SUPPLIER | M/s. AL ARABIA FOR SAFETY & SECURITY LLC
FIRE ALARM SYSTEM MANUFACTURER | M/s. EDWARDS System Technology
SUBMITTAL TITLE: | FIRE ALARM, VOICE EVACUATION & FIRE TELEPHONE SYSTEM
DATE: | 10.08.2026
MAIN FACP BATTERY CALCULATION GROUND FLOOR - FCC ROOM
STANDBY CURRENT (mA) | ALARM CURRENT (mA) | PART NO. | DESCRIPTION | QTY. | TOTAL STANDBY (mA) | TOTAL STANDBY (mA)
211 | 211 | 4-CPU | Central Processor Unit Module | 1 | 211 | 211
45 | 45 | 4-PPS | Primary Power Supply | 1 | 45 | 45
264 | 336 | 3-SDDC2 | Dual Loop SIGA Data Controller | 5 | 1320 | 1680
40 | 93 | 4-LCDLE | Liquid Crystal Module | 1 | 40 | 93
5 | 5 | 4-NET-TP | SFP Network controller | 2 | 10 | 10
130 | 130 | 4-FWAL4 | Network Firewalls | 1 | 130 | 130
62 | 1120 | 3-ZA20A | Zoned Audio Amplifiers | 2 | 124 | 2240
101 | 85 | 4-AUDTELS | Audio-Telephone Interface Module | 1 | 101 | 85
8 | 38 | 4-MIC | Paging Microphone | 1 | 8 | 38
9 | 168 | 4-FT | Firefighter Master Handset | 1 | 9 | 168
Notes: 1- The calculation has been carried out based on the full-load condition. The current consumption of 3-SDDC2 Dual Loop Cards has been considered based on a maximum of 500 connected devices, including all detectors and modules. 2- A separate cabinet is provided for the NAC circuits, utilizing SIGA-BPS10A/230. Refer to the NAC Circuit Calculation and SIGA-BPS10A/230 Battery Calculation for details. 3- A separate cabinet is provided for the VES circuits, utilizing SIGA-APS6A/230. Refer to the VES Circuit Calculation and SIGA-APS6A/230 Battery Calculation for details. 4- 24 hours of standby operation and 30 minutes of alarm operation have been considered in the battery calculations, in accordance with DCD requirements and NFPA 72 standards. |  |  | TOTAL STANDBY CURRENT (mA) |  | 1998
|  |  |  | TOTAL ALARM CURRENT (mA) |  | 4700
|  |  | TOTAL STANDBY CURRENT (mA) * 24h |  |  | 47952
|  |  | TOTAL ALARM CURRENT (mA) * 30m |  |  | 2350
|  |  | SUM TOTAL STANDBY + TOTAL ALARM (A) |  |  | 50.302
|  |  | TOTAL + 20% SPARE |  |  | 60.3624
|  |  | SELECTED BATTERY SIZE |  |  | 2 NOS 65AH

## sub
EDWARDS | PROJECT : Samana IVY Garden-2 (1B+G+4P+35+Roof) Residential Building @ PLOT NO: 648-8523, Wadi Al Safa 5, DLRC, Dubai, UAE |  |  |  |  | EST4
CLIENT | M/s. Samana IFM Holding Ltd
CONSULTANT | M/s. Al Hilal Engineering Consultant
MEP CONTRACTOR | M/s. ITALTECH CONTRACTING L.L.C
FIRE ALARM SYSTEM SUPPLIER | M/s. AL ARABIA FOR SAFETY & SECURITY LLC
FIRE ALARM SYSTEM MANUFACTURER | M/s. EDWARDS System Technology
SUBMITTAL TITLE: | FIRE ALARM, VOICE EVACUATION & FIRE TELEPHONE SYSTEM
DATE: | 10.08.2026
SUB FACP BATTERY CALCULATION 9th floor - Telephone room
STANDBY CURRENT (mA) | ALARM CURRENT (mA) | PART NO. | DESCRIPTION | QTY. | TOTAL STANDBY (mA) | TOTAL STANDBY (mA)
211 | 211 | 4-CPU | Central Processor Unit Module | 1 | 211 | 211
45 | 45 | 4-PPS | Primary Power Supply | 1 | 45 | 45
264 | 336 | 3-SDDC2 | Dual Loop SIGA Data Controller | 5 | 1320 | 1680
40 | 93 | 4-LCDLE | Liquid Crystal Module | 1 | 40 | 93
5 | 5 | 4-NET-TP | SFP Network controller | 2 | 10 | 10
Notes: 1- The calculation has been carried out based on the full-load condition. The current consumption of 3-SDDC2 Dual Loop Cards has been considered based on a maximum of 500 connected devices, including all detectors and modules. 2- A separate cabinet is provided for the NAC circuits, utilizing SIGA-BPS10A/230. Refer to the NAC Circuit Calculation and SIGA-BPS10A/230 Battery Calculation for details. 3- A separate cabinet is provided for the VES circuits, utilizing SIGA-APS6A/230. Refer to the VES Circuit Calculation and SIGA-APS6A/230 Battery Calculation for details. 4- 24 hours of standby operation and 30 minutes of alarm operation have been considered in the battery calculations, in accordance with DCD requirements and NFPA 72 standards. |  |  | TOTAL STANDBY CURRENT (mA) |  | 1626
|  |  |  | TOTAL ALARM CURRENT (mA) |  | 2039
|  |  | TOTAL STANDBY CURRENT (mA) * 24h |  |  | 39024
|  |  | TOTAL ALARM CURRENT (mA) * 30m |  |  | 1019.5
|  |  | SUM TOTAL STANDBY + TOTAL ALARM (A) |  |  | 40.0435
|  |  | TOTAL + 20% SPARE |  |  | 48.0522
|  |  | SELECTED BATTERY SIZE |  |  | 2 NOS 42AH

## sub (2)
EDWARDS | PROJECT : Samana IVY Garden-2 (1B+G+4P+35+Roof) Residential Building @ PLOT NO: 648-8523, Wadi Al Safa 5, DLRC, Dubai, UAE |  |  |  |  | EST4
CLIENT | M/s. Samana IFM Holding Ltd
CONSULTANT | M/s. Al Hilal Engineering Consultant
MEP CONTRACTOR | M/s. ITALTECH CONTRACTING L.L.C
FIRE ALARM SYSTEM SUPPLIER | M/s. AL ARABIA FOR SAFETY & SECURITY LLC
FIRE ALARM SYSTEM MANUFACTURER | M/s. EDWARDS System Technology
SUBMITTAL TITLE: | FIRE ALARM, VOICE EVACUATION & FIRE TELEPHONE SYSTEM
DATE: | 10.08.2026
SUB FACP BATTERY CALCULATION 20th floor - Telephone room
STANDBY CURRENT (mA) | ALARM CURRENT (mA) | PART NO. | DESCRIPTION | QTY. | TOTAL STANDBY (mA) | TOTAL STANDBY (mA)
211 | 211 | 4-CPU | Central Processor Unit Module | 1 | 211 | 211
45 | 45 | 4-PPS | Primary Power Supply | 1 | 45 | 45
264 | 336 | 3-SDDC2 | Dual Loop SIGA Data Controller | 5 | 1320 | 1680
40 | 93 | 4-LCDLE | Liquid Crystal Module | 1 | 40 | 93
5 | 5 | 4-NET-TP | SFP Network controller | 2 | 10 | 10
Notes: 1- The calculation has been carried out based on the full-load condition. The current consumption of 3-SDDC2 Dual Loop Cards has been considered based on a maximum of 500 connected devices, including all detectors and modules. 2- A separate cabinet is provided for the NAC circuits, utilizing SIGA-BPS10A/230. Refer to the NAC Circuit Calculation and SIGA-BPS10A/230 Battery Calculation for details. 3- A separate cabinet is provided for the VES circuits, utilizing SIGA-APS6A/230. Refer to the VES Circuit Calculation and SIGA-APS6A/230 Battery Calculation for details. 4- 24 hours of standby operation and 30 minutes of alarm operation have been considered in the battery calculations, in accordance with DCD requirements and NFPA 72 standards. |  |  | TOTAL STANDBY CURRENT (mA) |  | 1626
|  |  |  | TOTAL ALARM CURRENT (mA) |  | 2039
|  |  | TOTAL STANDBY CURRENT (mA) * 24h |  |  | 39024
|  |  | TOTAL ALARM CURRENT (mA) * 30m |  |  | 1019.5
|  |  | SUM TOTAL STANDBY + TOTAL ALARM (A) |  |  | 40.0435
|  |  | TOTAL + 20% SPARE |  |  | 48.0522
|  |  | SELECTED BATTERY SIZE |  |  | 2 NOS 42AH

## sub (3)
EDWARDS | PROJECT : Samana IVY Garden-2 (1B+G+4P+35+Roof) Residential Building @ PLOT NO: 648-8523, Wadi Al Safa 5, DLRC, Dubai, UAE |  |  |  |  | EST4
CLIENT | M/s. Samana IFM Holding Ltd
CONSULTANT | M/s. Al Hilal Engineering Consultant
MEP CONTRACTOR | M/s. ITALTECH CONTRACTING L.L.C
FIRE ALARM SYSTEM SUPPLIER | M/s. AL ARABIA FOR SAFETY & SECURITY LLC
FIRE ALARM SYSTEM MANUFACTURER | M/s. EDWARDS System Technology
SUBMITTAL TITLE: | FIRE ALARM, VOICE EVACUATION & FIRE TELEPHONE SYSTEM
DATE: | 10.08.2026
SUB FACP BATTERY CALCULATION 30th floor - Telephone room
STANDBY CURRENT (mA) | ALARM CURRENT (mA) | PART NO. | DESCRIPTION | QTY. | TOTAL STANDBY (mA) | TOTAL STANDBY (mA)
211 | 211 | 4-CPU | Central Processor Unit Module | 1 | 211 | 211
45 | 45 | 4-PPS | Primary Power Supply | 1 | 45 | 45
264 | 336 | 3-SDDC2 | Dual Loop SIGA Data Controller | 3 | 792 | 1008
40 | 93 | 4-LCDLE | Liquid Crystal Module | 1 | 40 | 93
5 | 5 | 4-NET-TP | SFP Network controller | 2 | 10 | 10
Notes: 1- The calculation has been carried out based on the full-load condition. The current consumption of 3-SDDC2 Dual Loop Cards has been considered based on a maximum of 500 connected devices, including all detectors and modules. 2- A separate cabinet is provided for the NAC circuits, utilizing SIGA-BPS10A/230. Refer to the NAC Circuit Calculation and SIGA-BPS10A/230 Battery Calculation for details. 3- A separate cabinet is provided for the VES circuits, utilizing SIGA-APS6A/230. Refer to the VES Circuit Calculation and SIGA-APS6A/230 Battery Calculation for details. 4- 24 hours of standby operation and 30 minutes of alarm operation have been considered in the battery calculations, in accordance with DCD requirements and NFPA 72 standards. |  |  | TOTAL STANDBY CURRENT (mA) |  | 1098
|  |  |  | TOTAL ALARM CURRENT (mA) |  | 1367
|  |  | TOTAL STANDBY CURRENT (mA) * 24h |  |  | 26352
|  |  | TOTAL ALARM CURRENT (mA) * 30m |  |  | 683.5
|  |  | SUM TOTAL STANDBY + TOTAL ALARM (A) |  |  | 27.0355
|  |  | TOTAL + 20% SPARE |  |  | 32.4426
|  |  | SELECTED BATTERY SIZE |  |  | 2 NOS 42AH

## APS
EDWARDS | PROJECT : Samana IVY Garden-2 (1B+G+4P+35+Roof) Residential Building @ PLOT NO: 648-8523, Wadi Al Safa 5, DLRC, Dubai, UAE |  |  |  |  | EST4
CLIENT | M/s. Samana IFM Holding Ltd
CONSULTANT | M/s. Al Hilal Engineering Consultant
MEP CONTRACTOR | M/s. ITALTECH CONTRACTING L.L.C
FIRE ALARM SYSTEM SUPPLIER | M/s. AL ARABIA FOR SAFETY & SECURITY LLC
FIRE ALARM SYSTEM MANUFACTURER | M/s. EDWARDS System Technology
SUBMITTAL TITLE: | FIRE ALARM, VOICE EVACUATION & FIRE TELEPHONE SYSTEM
DATE: | 10.08.2026
APS BATTERY CALCULATION
STANDBY CURRENT (mA) | ALARM CURRENT (mA) | PART NO. | DESCRIPTION | QTY. | TOTAL STANDBY (mA) | TOTAL STANDBY (mA)
2 | 2800 | 3-AA50 | Intelligent Audio Amplifiers | 2 | 4 | 5600
200 | 200 | Auxiliary output | Auxiliary output | 1 | 200 | 200
0.00396 | 0.0068 | SIGA-CT2 | Dual Monitor Module | 1 | 0.00396 | 0.0068
Notes: The calculation has been carried out based on the full-load condition. The current consumption of 3-AA50 Intelligent Audio Amplifiers has been considered based on a maximum load of 50 W per amplifier. The battery calculation has been carried out considering 24 hours of standby operation and 30 minutes of alarm operation, in accordance with DCD requirements and NFPA 72 standards. |  |  | TOTAL STANDBY CURRENT (mA) |  | 204.004
|  |  |  | TOTAL ALARM CURRENT (mA) |  | 5800.0068
|  |  | TOTAL STANDBY CURRENT (mA) * 24h |  |  | 4896.095
|  |  | TOTAL ALARM CURRENT (mA) * 30m |  |  | 2900.0034
|  |  | SUM TOTAL STANDBY + TOTAL ALARM (A) |  |  | 7.7961
|  |  | TOTAL + 20% SPARE |  |  | 9.3553
|  |  | SELECTED BATTERY SIZE |  |  | 2 NOS 7AH

## BPS
EDWARDS | PROJECT : Samana IVY Garden-2 (1B+G+4P+35+Roof) Residential Building @ PLOT NO: 648-8523, Wadi Al Safa 5, DLRC, Dubai, UAE |  |  |  |  | EST4
CLIENT | M/s. Samana IFM Holding Ltd
CONSULTANT | M/s. Al Hilal Engineering Consultant
MEP CONTRACTOR | M/s. ITALTECH CONTRACTING L.L.C
FIRE ALARM SYSTEM SUPPLIER | M/s. AL ARABIA FOR SAFETY & SECURITY LLC
FIRE ALARM SYSTEM MANUFACTURER | M/s. EDWARDS System Technology
SUBMITTAL TITLE: | FIRE ALARM, VOICE EVACUATION & FIRE TELEPHONE SYSTEM
DATE: | 10.08.2026
BPS BATTERY CALCULATION
STANDBY CURRENT (mA) | ALARM CURRENT (mA) | PART NO. | DESCRIPTION | QTY. | TOTAL STANDBY (mA) | TOTAL STANDBY (mA)
70 | 10270 | BPS10A | 10 amp Booster | 1 | 70 | 10270
Notes: The calculation has been carried out based on the full-load condition. The current consumption of BPS10A, 10 amp Booster power supply has been considered based on a maximum load of 10 A. The battery calculation has been carried out considering 24 hours of standby operation and 30 minutes of alarm operation, in accordance with DCD requirements and NFPA 72 standards. |  |  | TOTAL STANDBY CURRENT (mA) |  | 70
|  |  |  | TOTAL ALARM CURRENT (mA) |  | 10270
|  |  | TOTAL STANDBY CURRENT (mA) * 24h |  |  | 1680
|  |  | TOTAL ALARM CURRENT (mA) * 30m |  |  | 5135
|  |  | SUM TOTAL STANDBY + TOTAL ALARM (A) |  |  | 6.815
|  |  | TOTAL + 20% SPARE |  |  | 8.178
|  |  | SELECTED BATTERY SIZE |  |  | 2 NOS 7AH